Proceedings of:

ASME TURBO EXPO 2003

June 16–19, 2003 — Atlanta, Georgia, USA

GT2003-38191

OPTiMIZED OPERATING POINT SELECTION FOR GAS TURBINE HEALTH STATE ANALYSIS BY USING A MULTI-POINT TECHNIQUE

| ## M. Pinelli Dip. di Ingegneria – University of Ferrara Via Saragat, 1 - 44100 Ferrara, Italy | P.R. Spina DIEM - University of Bologna Viale del Risorgimento, 2 – 40136 Bologna, Italy |
| --- | --- |

|  | ## M. Venturini Dip. di Ingegneria – University of Ferrara Via Saragat, 1 - 44100 Ferrara, Italy |  |
| --- | --- | --- |

Abstract

Gas turbine operating state determination can be performed using Gas Path Analysis (GPA) techniques, which use measurements taken on the machine to calculate the characteristic parameters that are indices of the machine health state. The number and type of characteristic parameters that can be evaluated depend on the number and type of the available measured variables. Thus, when there are not enough measured variables to determine all the characteristic parameters, some of them have to be estimated independently of the actual gas turbine health state. In this way, variations due to aging or deterioration which, in the actual machine, may occur on these last characteristic parameters, cause estimation errors on the characteristic parameters assumed as problem unknowns.

The available instrumentation in field applications is often inadequate to ensure reliable operating state analysis when GPA-based techniques are used. This problem may be partially overcome using a multiple operating point minimization technique. This consists of the determination of the characteristic parameters that minimize the sum of the square differences between measured and computed values of the measurable variables in multiple operating points. In this way the lack of data is overcome by data obtained in different operating points.

This paper describes a procedure for gas turbine operating state determination based on a multiple operating point minimization technique and presents a study aimed at selecting the best set and number of operating points that should be used.

introduction

Gas turbine operating state determination can be performed by means of Gas Path Analysis (GPA) techniques, which use measurements taken on the machine to calculate the characteristic parameters that are indices of the machine health state, as, for example, efficiencies and characteristic flow passage areas of compressor and turbines, combustor efficiency and pressure drops along the gas path. These techniques often use a computational mathematical model of the gas turbine thermodynamic cycle (Cycle Program) which is solved in inverse mode to estimate the characteristic parameters [1-3]. The inverse solution is usually performed to reproduce the actual measurements taken in a single gas turbine Operating Point (OP).

The reliability of the characteristic parameter estimation obtained in this way depends on many factors, such as [4]:

- the capability of the Cycle Program to accurately reproduce the machine performances in "new and clean" conditions;

- the reliability of the field measurements;

- the instrumentation available on the gas turbine, which limits the number of characteristic parameters which can be determined. In fact, the number and type of characteristic parameters that can be evaluated depend on the number and type of the available measured variables. Thus, when the number of measured variables is not sufficient to determine all the characteristic parameters, some of them have to be estimated independently of the actual gas turbine health state. In this way, variations due to aging or deterioration which, in the actual machine, may occur on these last characteristic parameters, cause estimation errors on the characteristic parameters assumed as problem unknowns.

In the field application of GPA techniques, both the available information about the gas turbine and the measured variables are often inadequate to ensure a reliable operating state analysis. In fact, the compressor and turbine performance maps are usually not provided by the gas turbine manufacturer. So the Cycle Program has to be set up by using the little information available, such as (i) the performance data at ISO condition, (ii) the correction curves for compensating the effect of ambient conditions (ambient temperature, pressure and relative humidity), pressure loss and load condition and (iii) the measurements taken during the acceptance tests. Moreover, the poor instrumentation usually available on the gas turbine requires some key parameters to be estimated independently of the machine health state, leading to the above mentioned uncertainties in the parameter estimation.

These problems may be partially overcome using a multiple operating point minimization technique. This consists of the determination of the characteristic parameters that minimize the sum of the square differences between measured and computed values of the measurable variables in multiple operating points. In this way the lack of data is overcome by data obtained in different operating points [5,6]. Such a technique can be easily applied when the machine performance tests are performed, since on such occasions measurements at different loads are usually available.

It can be noted that the procedures for Cycle Program set up and for gas turbine operating state determination are similar, since, in both cases, the gas turbine characteristic parameters have to be determined starting from an initial guess value of the parameters themselves and from a reduced set of available data. Therefore, the benefits which can be obtained in gas turbine operating state determination by using the multiple operating point minimization technique, can also be extended to the case of the Cycle Program set up.

This paper describes a procedure for gas turbine operating state determination based on a multiple operating point minimization technique. In particular, the aim of the paper is to carry out a comprehensive study aimed at selecting the number of operating points that should be used and their best combination within the whole gas turbine operating range. In fact, this type of analysis, which has not been thoroughly carried out before, can give useful information for the field application of the multiple operating point minimization technique, in order to maximize the accuracy in gas turbine operating state determination.

Nomenclature

CGL	Center of Gravity of the Load combination

Fob	objective function

M	mass flow rate

N	rotational speed

Nc	number of constraint equations

Nlc	number of load combinations

Nm	dimension of Qm vector

Nop	number of operating points

Nwp	dimension of Qwp vector

Nx	dimension of X vector

p	total pressure

Pel	electric power

Qm	vector of measured variables

Qm,c	vector of computed estimates of the measured variables

Qwp	vector of measured variables necessary to define the working point

RH	relative humidity

RRI	Relative Redundancy Index

RMS	Root Mean Square

SDL	Standard deviation of Load combination

T	total temperature

VN	variable nozzle angular position

w	weight

X	vector of unknown characteristic parameters

β	pressure ratio

	variation

	efficiency

	= MTp corrected mass flow rate

	= NT corrected rotational speed

### Subscripts and Superscripts

*	normalized value with respect to the reference value in “new and clean” condition

a	ambient

A	average

c	computed value

c	compressor

cc	combustor

e	expected value

f	fuel

ggt	gas generator turbine

o	outlet section

pt	power turbine

r	reference value

r_0	reference value in the "new and clean" condition

PROBLEMS IN GAS TURBINE OPERATING STATE DETERMINATION

Gas turbine operating state determination consists in the assessment of the modification, due to deterioration and fault, of performance and geometric data characterizing the machine components. One of the main effects of deterioration and fault is the modification of compressor and turbine performance maps. Since exact information about actual modification of component maps is usually not available, many authors simulate the effects of deterioration and fault by a simple shift of the map itself [1,3,6]. The shift of actual compressor and turbine performance maps with respect to "new and clean" condition can be assessed by calculating the actual value of map "scale factors", which are the parameters used to build the performance maps in non-dimensional form [3]. For example, Fig. 1 shows the non-dimensional maps of a multistage axial-flow compressor with transonic stages [7]: the relative pressure variation through the compressor (C-1), and the efficiency, are related to corrected mass flow and corrected rotational speed. In these maps, the "scale factors" are the reference values of the relative pressure variation ((C-1)r), of the compressor efficiency ((C)r), of the corrected mass flow ((C)r) and of the corrected rotational speed ((C)r). If these values change, the dimensional map data (obtained by multiplying the

Fig. 1 - Efficiency and corrected mass flow compressor maps. 
( ― ) "new and clean" condition; ( ---- ) 2 % reduction of the "scale factors"

non-dimensional map data by the "scale factors") change proportionally. Therefore, the performance map shift due to deterioration and fault can be represented by a variation of the map "scale factors". For example, in Fig. 1 the effects of a 2 % reduction of the "scale factors" of compressor efficiency and corrected mass flow rate are shown.

Therefore, the "scale factors" of efficiency and corrected mass flow of compressor and turbines ((C)r, (C)r, (GGT)r, (GGT)r, (PT)r and (PT)r) can be assumed as compressor and turbine characteristic parameters. In addition to these characteristic parameters, two other important parameters for representing the gas turbine health state are the combustor efficiency CC and pressure drop pCC. In particular, CC accounts for thermal losses along the gas path, which are considered as a fixed constant percentage of the thermal power introduced by the fuel, while pCC is defined as a constant percentage of the total pressure at the combustor inlet [1, 3]. It can be noted that this type of characteristic parameter is sensitive to the gas turbine health state, while it is not dependent on the gas turbine operating point. Parameters with this characteristic are usually called Health Indices.

The characteristic parameters can be calculated by solving in inverse mode the program for gas turbine thermodynamic cycle calculation. Considering that the values of the measurable variables computed by the Cycle Program Qm,c are a function of the machine characteristic parameters X and of the values assumed by the variables that unequivocally determine the operating point at which the gas turbine is working Qwp, the following equation can be written:

Qm,c=f(X,Qwp)	(1),

By inverting Eq. (1), it is possible to calculate the characteristic parameters starting from the measured variables:

X=F(Qm, Qwp)	(2).

From Eq. (2), the number and type of gas turbine characteristic parameters that can be determined for each operating point (i.e. for each set of Qwp) depend on the number and type of equations, which, in turn, depend on the number and type of the available measured variables. In particular, the number of characteristic parameters is generally equal to the number of the Qm measured variables. So, since the number of the Qm available measured variables is usually lower than the number of characteristic parameters to be estimated, some of them have to be kept constant during the calculations. Therefore, variations due to aging or deterioration which, in the actual machine, occur on the characteristic parameters which were considered as fixed parameters, will cause an estimation error on the characteristic parameters to be determined [4].

Furthermore, more equations can be obtained from Eq. (2) by using more than one Qwp set and, thus, the number of gas turbine characteristic parameters that can be determined also depends on the number of gas turbine operating points (i.e. number of Qwp sets) [5]. Therefore, by using multiple operating points it is possible to evaluate a number of characteristic parameters higher than the number of the available Qm measured variables.

The operating points have to be taken within a small time interval (for instance during the same day) so that the gas turbine health state can be considered the same for all the operating points and, thus, the solution X of Eq. (2) is the same for all the operating points.

In particular, the equation system redundancy due to the use of multiple operating points can be quantified by using the Relative Redundancy Index introduced by Zedda and Singh [8]:

(3),

where Nop is the number of operating points, Nm the number of Qm measured variables, Nwp the number of Qwp measured variables and Nx the number of characteristic parameters X that have to be determined.

Zedda and Singh [8] demonstrated that accuracy in parameter determination increases when the RRI value increases. For given Nm, Nwp and Nx, the RRI value can be increased if Nop is augmented. However, the computational effort increases and convergence can be reached with greater difficulty. Moreover, by augmenting Nop the rate of increase of RRI decreases. The above considerations lead to a limitation of the number of operating points.

In conclusion, the multiple operating point minimization technique allows the calculation of a number of characteristic parameters greater than the number of the available measured variables. The sections below report the results of an analysis developed in order to determine the best set and number of operating points that should be used.

MULTIPLE OPERATING POINT MINIMIZATION TECHNIQUE

The multiple operating point minimization technique presented in this paper determines the values of gas turbine characteristic parameters that minimize the sum of the square differences, between measured and computed values of the measurable variables, in multiple operating points. This problem is solved by using a non-linear algorithm which minimizes the objective function:

Fob(X1,...,XNx)=1Nopj=1Nopi=1NmwiQm,c−QmQmi2j	(4),

where Xi (i=1,..,Nx) are the unknown parameters, (Qm,c)i and (Qm)i are the computed estimates and the measured values of the measurable variables respectively, and wi are the weights assigned to each term of the objective function. In particular:

- the Qm,c values are an implicit function of the X parameters and are evaluated by running the Cycle Program for each operating point;

- as weights wi values proportional to the inverse of the uncertainty of the corresponding measurement are used.

The main steps of the multiple operating point technique are sketched in Fig. 2.

In order to improve the minimization algorithm convergence, constraint equations can be added so that, in some operating points, the computed estimates of the measurable variables are imposed equal to the corresponding measured values [9]:

Qm,c−QmQmij=0   ,   i=1,...,Nm;   j=1,...,Nc	(5),

where Nc  Nop.

Figure 2 – Multiple operating point minimization technique

The constraints are usually imposed at the operating points which have to be reproduced as accurately as possible.

The constrained minimization algorithm which was used is contained in the IMSL math library [10] and was successfully utilized by the authors to solve, in direct and inverse mode, the gas turbine mathematical model [3,9,11,12,13,14].

ANALYSIS OF THE INFLUENCE OF OPERATING POINT SELECTION

For the analysis of the influence of operating point selection the Cycle Program of a 10 MW two shaft heavy-duty industrial gas turbine with variable power turbine nozzle [7] used as generator drive was used.

As reported in Table 1, the considered measurement set is composed of five Qm measured variables: pressure and temperature at the compressor outlet (poC, ToC), fuel mass flow rate (Mf), turbine outlet temperature (ToPT) and variable turbine nozzle angular position (VN). This can be considered a common situation in practice for a two shaft gas turbine with variable power turbine nozzle [4,15]. The characteristic parameters, indices of gas turbine health state, which were considered as problem variables, are the "scale factors" of compressor, gas generator and power turbine efficiency and corrected mass flow rate ((C)r, (C)r, (GGT)r, (GGT)r, (PT)r and (PT)r) and the combustor efficiency (CC).

The simulations were performed as follows:

- the availability of a different number of OPs (i.e. Nop=2, 3, 4 and 5) was assumed. The OPs differ from each other only with respect to the load, ranging from 70 % to 100 % of the full load.

- For each OP, the values of the measured variables, which correspond to a gas turbine malfunction, were obtained by running the Cycle Program in direct mode, for an imposed variation of the characteristic parameters, as explained below (Table 3).

- In order to account for measurement uncertainty, which always affects field measurements, each computed value of the measurable variables was corrupted with a random error contained in the ranges reported in Table 2. These ranges were considered according to the guidelines reported in the ISO 2314 International Standard [16]. For some measurements the uncertainty was considered higher than that reported in the ISO 2314, since it was assumed that measurements were taken in the field with standard machine instrumentation during normal operation and not when conducting an acceptance test [17].

Table 1 - Available measurements and calculated

characteristic parameters

| Qwp measurements | Qm measurements | Characteristic parameters X |
| --- | --- | --- |
| Pel | poC | (C)r |
| NGGT | ToC | (C)r |
| NPT | Mf | (GGT)r |
| Ta | ToPT | (GGT)r |
| pa | VN | (PT)r |
| RH |  | (PT)r |
|  |  | CC |

Table 2 – Measurement uncertainty

| Measurement | [%] |
| --- | --- |
| poC | 0.40 |
| Mf | 2.00 |
| VN | 1.00 |
| pa | 0.10 |
| RH | 3.00 |
| Pel | 0.50 |
| NGGT | 0.25 |
| NPT | 0.25 |

| Measurement | [K] |
| --- | --- |
| ToC | 3.0 |
| ToPT | 4.0 |
| Ta | 1.0 |

- For any given Nop, different load combinations were considered. Each combination is characterized by a Center of Gravity of the Load combination (CGL) and by its Standard Deviation (SDL) value, the former defining the center of gravity of the OPs, the latter representing the OP scatter with respect to the center of gravity:

CGL=i=1NopPeliNop	(6)

SDL=i=1NopPeli−CGL2Nop	(7)

- The program was finally run in inverse mode to calculate the characteristic parameters. A value of the Fob smaller than 10-3 was considered for convergence. In order to improve the minimization algorithm convergence, constraint equations (Eq. (5)) for the operating point at full load were used: this operating point was considered in all the load combinations.

To evaluate the error in the characteristic parameter calculation, three different indices were considered.

The first index, which represents an average root mean square error of the estimation [18], was calculated for a given number of OPs and for a given load combination:

RMSjk=i=1NxXci−Xei2Nx  , j=1,...,Nlck ,  k=1,...,Nop   (8)

where Xc is the characteristic parameter vector calculated by running the program in inverse mode, while Xe is the vector of the expected values of the characteristic parameters which was used for the direct calculation.

The second index was calculated for each Nop as the average root mean square value for all the load combinations:

RMSAk=j=1NlckRMSjkNlck   ,   k=1,...,Nop	(9)

The third index represents the error in the characteristic parameter calculation averaged for all the load combinations, and it was evaluated for each characteristic parameter and for each Nop:

ΔXiAk=j=1NlckXci−XeijNlck    ,   i=1,...,Nx   ,   k=1,...,Nop    (10)

### Characteristic parameter initial guess value influence

In order to establish whether the equation system (Eq. (2)), representing the inverse solution of the gas turbine thermodynamic cycle is determined, an analysis was performed to assess the influence of the choice of the characteristic parameter initial guess values on the final values obtained when the minimization algorithm reaches convergence.

The inverse calculations were performed using as input the computed values of the measurable variables, obtained by running the Cycle Program in direct mode, without measurement errors and in the case of no fault (i.e., all the normalized characteristic parameters are equal to one). The inverse calculations were performed from one to five operating points with different initial X guess values, and a value of the Fob smaller than 10-6 was, for these calculations, considered for convergence.

It can be noticed from Fig. 3 that the case of 1 OP is not determined, since the calculated characteristic parameter values depend on the initial guess value. Thus, the calculations for the case of 1 OP are not reported in the following sections. On the other hand, when at least 2 OPs are used, the equation system is determined and the parameters are reproduced with good accuracy, independently of the initial guess value. In Fig. 3, the results for 4 and 5 OPs are not reported, since, for these cases, the Relative Redundancy Index is even greater, and, thus, the equation system can be considered determined with certainty.

The same calculations were also performed by using, as inputs, the computed values of the measurable variables corrupted with random measurement errors. In this case, due to measurement errors, the Fob values considered for convergence were higher than in the previous case (Fob < 10-3). The results are shown in Fig. 4. The presence of the measurement errors increases the uncertainty in the characteristic parameter calculation, but the uncertainty is reduced when the number of operating points increases. It can be noted how the uncertainty reduction rate becomes negligible when Nop passes from 4 to 5.

Figure 3 –Parameter initial guess value influence

(without measurement errors)

Figure 4 –Parameter initial guess value influence

(with measurement errors)

### Uncertainty in the characteristic parameter calculation

Case 1 – No Fault Condition. The calculations were performed considering the gas turbine in "new and clean" conditions (No Fault) and corrupting the computed values of the measurable variables with random errors contained in the ranges reported in Table 2.

Figure 5 shows that the RMSA values reduce when the number of operating points increases and that this reduction becomes negligible for Nop > 3. The same considerations are emphasized by analyzing Fig. 6, which reports the errors in the characteristic parameter calculation defined in Eq. (10).

In Figs. 7 and 8, the RMS values, normalized with respect to their maximum value, are reported for each Nop versus CGL and SDL, respectively. It can be noticed that the (RMS, CGL) distribution shows an increasing trend while the (RMS, SDL) distribution shows a decreasing trend. Thus, the best load combination should be characterized by the lowest values of CGL and by the highest values of SDL, i.e. a load combination allowing good accuracy should have a high number of low power operating points.

The results obtained by using the multiple operating point minimization technique can be compared to those obtained by using a single operating point. In the single operating point calculation, the problem has to be rendered determined by keeping constant two characteristic parameters. In particular two cases were considered, the first in which CC and (PT)r were kept constant, the second in which CC and (PT)r were instead kept constant [4]. Only full load operation was considered in both simulations and the results, in terms of RMS and errors in the characteristic parameter calculation X*i, are reported in Fig. 9. The comparison with the corresponding results reported in Figs. 5 and 6 highlights how the errors obtained in the single operating point cases are lower than those obtained by using the multiple operating point technique with Nop = 2. If Nop > 2, the results obtained by using the multiple operating point technique are instead better than those obtained in the single operating point cases. This is due to the fact that, with the multiple operating point technique, the measurement errors can be spread among a greater number of variable parameters. For example, an error on the Mf measurement, mainly affects the CC value with the multiple operating point technique, while, in the case of a single operating point, it strongly affects more than one characteristic parameter [4].

Figure 5 – No Fault: RMS Mean Value RMSA

Figure 6 – No Fault: X*iA

Figure 7 – No Fault: Normalized RMS versus CGL

Figure 8 – No Fault: Normalized RMS versus SDL

Figure 9 – No Fault: RMS and X*i values for the case of five variable characteristic parameters

Case 2 – Fault Condition. Gas turbine malfunctions were simulated by imposing the variations of the characteristic parameters reported in Table 3.

Two malfunctions were considered: Fault 1, which simulates a generalized condition of malfunction for the whole gas turbine, and Fault 2, which, in addition to the characteristic parameter variations of Fault 1, also considers a variation of the combustor efficiency. This permits the estimation errors on the thermal power introduced into the gas turbine to be taken into account. This is a particularly critical quantity due to the uncertainties on the fuel mass flow rate measurement and on the lower heating value estimation. For 2, 3, 4 and 5 OPs, different load combinations were considered, each of them containing the operating point at full load.

The results obtained are reported in Figs. 10 to 13 and in Figs. 14 to 17 for Fault 1 and Fault 2 respectively. From 
Figs. 10 and 14 (for Fault 1 and Fault 2 respectively) it can be seen that RMSA values reduce when the number of the operating points increases. The RMSA reduction rate tends to be negligible by augmenting the number of operating points. In all the cases reported in the paper (No Fault, Fault 1 and Fault 2), the RMSA values obtained for Nop = 4 are close to a minimum limit to which RMSA tends by augmenting the number of operating points. The value of this limit depends on the magnitude of measurement errors.

Table 3 – Imposed characteristic parameter variations

for the simulated faults

|  | Characteristic parameter variation [% reference value] |  |
| --- | --- | --- |
|  | FAULT 1 | FAULT 2 |
| C | -2 | -2 |
| C | -5 | -5 |
| GGT | -2 | -2 |
| GGT | +2 | +2 |
| PT | -2 | -2 |
| PT | +2 | +2 |
| CC | 0 | -2 |

Figure 10 – Fault 1: RMS Mean Value RMSA

Figure 11 – Fault 1: X*iA

Figure 12 – Fault 1: Normalized RMS versus CGL

Figure 13 – Fault 1: Normalized RMS versus SDL

Figure 14 – Fault 2: RMS Mean Value RMSA

Figure 15 – Fault 2: X*iA

Figure 16 – Fault 2: Normalized RMS versus CGL

Figure 17 – Fault 2: Normalized RMS versus SDL

Figure 18 – Fault 2: RMS and X*i values for the case of five variable characteristic parameters

The same considerations are emphasized by analyzing 
Figs. 11 and 15 for Fault 1 and Fault 2 respectively, which report the errors in the characteristic parameter calculation defined in Eq. (10).

Figures 12, 13, for Fault 1, and Figs. 16, 17, for Fault 2, which report the RMS values normalized with respect to their maximum value versus CGL and SDL respectively, confirm the results obtained in Figs. 7 and 8 (No Fault Condition). These figures highlight the fact that the best load combination is characterized by the lowest values of CGL and by the highest values of SDL.

As in the previous paragraph (No Fault), for Fault 2 the results obtained by using the multiple operating point minimization technique were compared to those obtained by using a single operating point. The two cases were considered in which CC and (PT)r or CC and (PT)r were kept constant to render the problem determined [4].

Also for Fault 2, for the single operating point cases only the full load operation was considered and the results, in terms of average root mean square error RMS and errors in the characteristic parameter calculation X*i, are reported in 
Fig. 18. The comparison with corresponding results reported in Figs. 14 and 15 highlights how the errors obtained in the single operating point cases considered are always much higher than those obtained by using the multiple operating point minimization technique. This is due to two factors [4]. First, with the multiple operating point technique, the error deriving from measurement uncertainty is spread over a higher number of characteristic parameters than in the single operating point case, as previously observed for the No Fault Condition. Second, the error due to the fact that in the single operating point calculations some parameters have to be kept constant, is avoided by using the multiple operating point minimization technique. In fact, variations on parameters that were kept constant in the single operating point case (such as, PT, PT and CC) cause an estimation error on the variable characteristic parameters. In the case of No Fault Condition, this effect was not discussed, since the characteristic parameters kept constant during the calculations were fixed at their initial values which were also the expected values (in No Fault Condition all parameters are expected to be equal to one).

The first application of the multiple operating point minimization technique to a real case was presented by the Authors in [13]. This application has highlighted the improvements of the reliability in gas turbine health state determination obtainable by using the multiple operating point minimization technique instead of a single operating point calculation.

## CONCLUSIONS

In this paper, a procedure for gas turbine operating state determination based on a multiple operating point minimization technique has been presented. The analysis which was carried out, demonstrates that the use of a multiple operating point minimization technique in gas turbine operating state assessment allows for the determination of a number of characteristic parameters (indices of gas turbine health state) which is higher than the number of available measured variables. For instance, in the analyzed cases of five available measured variables and seven unknown characteristic parameters, the case of single operating point analysis is not determined and so it is not possible to obtain a reliable determination of the characteristic parameters. By using the multiple operating point minimization technique, the problem of the seven characteristic parameter calculation is, instead, determined, by utilizing at least two operating points. Moreover, the accuracy in characteristic parameter determination can be substantially improved with respect to the case of a single operating point in which some characteristic parameters are kept constant to render the problem determined.

In addition, an analysis to determine the best set and number of operating points which should be used for gas turbine operating state determination was carried out. Two typologies of fault were simulated: one (Fault 1), which simulates a generalized condition of malfunction for the whole gas turbine, and the second (Fault 2) in which a variation of the combustor efficiency is also considered. The analyses were always carried out considering the presence of measurement uncertainty.

The results show that the average root mean square error RMSA decreases when the number of OPs increases, but its reduction rate decreases by augmenting the number of operating points. In fact, if 4 OPs are used, the obtained RMSA values are close to a minimum limit to which RMSA tends by augmenting the number of operating points. The value of this limit depends on the magnitude of measurement errors. Furthermore, the best load combinations are the ones characterized by the lowest values of CGL and by the highest values of SDL. These results were always confirmed in all the other cases analyzed, which were not reported in this paper.

Acknowledgments

The work was carried out with the support of the M.U.R.S.T. (Italian Ministry of University and Scientific & Technological Research).

References

- Stamatis, A., Mathioudakis, K., Papailiou, K.D., 1990, "Adaptive Simulation of Gas Turbine Performance", ASME Journal of Engineering for Gas Turbines and Power, 112, pp. 168-175.

- Benvenuti, E., Bettocchi, R., Cantore, G., Negri di Montenegro, G., Spina, P.R., 1993, "Gas Turbine Cycle Modeling Oriented to Component Performance Evaluation from Limited Design or Test Data", Proceedings, 7th ASME COGEN - TURBO, Bournemouth, UK, IGTI Vol. 8, pp. 327-337.

- Bettocchi, R., Spina, P. R., 1999, "Diagnosis of Gas Turbine Operating Conditions by Means of the Inverse Cycle Calculation", ASME Paper 99-GT-185.

- Pinelli, M., Spina, P. R., 2002, "Gas Turbine Field Performance Determination: Sources of Uncertainties", ASME Journal of Engineering for Gas Turbines and Power, 124, pp. 155-160.

- Stamatis, A., Papailiou, K.D., 1988, "Discrete Operating Conditions Gas Path Analysis", Proceedings, AGARD Conference, Quebec, Canada, pp. 33-1 - 33-10

- Gulati, A., Zedda, M., Singh, R., 2000, "Gas Turbine Engine and Sensor Multiple Operating Point Analysis Using Optimization Techniques", Proceedings, 36th AIAA/ASME/ SAE/ASEE Joint Propulsion Conference & Exibit, Huntsville, Alabama, USA, July 17 – 19, AIAA 2000-3716.

- Benvenuti, E. and Gusso, R., 1985, "Design and Development of the PGT10 Heavy-Duty Advanced Gas Turbine", ASME Paper 85-IGT-21.

- Zedda, M., Singh, R., 1999, " Gas Turbine Engine and Sensor Diagnostics", Proceedings, XIV International Symposium on Air-Breathing Engines (ISABE), Florence, Italy, September 5 - 10, IS10/UNK010.

- Bettocchi, R., Spina, P.R., Alliney, S., 1994, "Resolution Method for Gas Turbine Mathematical Models", Proceedings, 8th ASME COGEN - TURBO, Portland, Oregon, USA, IGTI Vol. 9, pp. 361-369.

- Visual Numerics, Inc., 1994, "IMSL MATH/LIBRARY: FORTRAN Subroutines for Mathematical Applications", Houston, Texas, USA.

- Benvenuti, E., Bettocchi, R., Cantore, G., Negri di Montenegro, G., Spina, P. R., 1994, "Experimental Validation of a Gas Turbine Cycle Model Based on a Simultaneous Solution Method", Proceedings, 8th ASME COGEN - TURBO, Portland, Oregon, USA, IGTI Vol. 9, pp. 245-255.

- Bettocchi, R., Spina, P. R., Benvenuti, E., 2000, "Set-Up of an Adaptive Method for the Diagnosis of Gas Turbine Operating State by Using Test-Bench Measurements", ASME Paper 2000-GT-0309.

- Bettocchi, R., Pinelli, M., Spina, P. R., Venturini, M., Sebastanelli, S., 2001, "A System for Health State determination of Natural Gas Compression Gas Turbines", ASME Paper 2001-GT-0223.

- Spina, P. R., 2002, "Gas Turbine Performance Prediction by Using Generalized Performance Curves of Compressor and Turbine Stages", ASME Paper GT-2002-30275.

- Pinelli, M., Venturini, M., 2001, "Improvement of the Accuracy in Gas Turbine Health Determination", ASME Paper 2001-GT-0476.

- ISO 2314, 1989, "Gas Turbine - Acceptance Tests", International Standard.

- Brun, K., Kurz, R., 2001, "Measurement Uncertainties Encountered During Gas Turbine Driven Compressor Field Testing", ASME Journal of Engineering for Gas Turbines and Power, 123, pp. 62-69.

- Stamatis, A., Mathioudakis, K., Papailiou, K., 1992, "Optimal Measurement and Health Index selection for Gas Turbine Performance Status and Fault Diagnosis", ASME Journal of Engineering for Gas Turbines and Power, Vol. 114, pp. 209-216.

When compressors with variable inlet guide vanes (VIGVs) or turbines with variable nozzles (VNs) are considered, a number of compressor or turbine performance maps relative to different VIGV or VN positions respectively are used. In this case all non-dimensional maps must be obtained from the dimensional data by using the same "scale factor" values, so that, also in this case, they are not dependent on the gas turbine operating point.